## Slide 1
TechHeads 2026
Glaze
Fredrik Svensson
Alexander Wallin
The city breathes Real-time AI control of district heating

## Slide 2: Who we are
Glaze — eleven years bringing IoT and AI to small and mid-size companies. Offices in Malmö and Denmark.
Beacon Tower is our platform for real-time data and AI on physical systems, built from the start for cost and automation — to make this affordable for the many, not just the few. A product in its own right, used across many industries (beacontower.io).
RACE — Real-time AI Computing in the Energy sector — is what we build on it for district heating, and the product we’re now bringing to market.

## Slide 3: District heating is a living system
Roughly half the heat in Sweden and Denmark flows through district heating: hot water pumped through kilometres of buried pipe.
It behaves like an organism: it breathes with the day and the seasons, it changes as it grows, and it reacts slowly — in minutes to hours, not seconds.
And most of it still runs on fixed schedules and operator experience — a living system that never learns to regulate itself.

## Slide 4: So what makes this hard?
A slow system, hard physical limits, and thousands of consumers to keep warm at once — the worst-served one sets the bar.
And you can’t experiment freely — get it wrong and people feel it, in a lukewarm shower or a cold radiator.

## Slide 5: Every building already has a meter
It only ever ticks upward. The slope is the demand — flat in summer, steep in winter. This is the data every grid already owns.

## Slide 6: This is what one building looks like
Real heat data from a single building (substation). No model yet — just what the sensors on the building see.

## Slide 7: Plot it against the weather, and it starts to make sense
The same messy demand, plotted against outdoor temperature. Out of the noise, a clear trend appears — colder means more heat.

## Slide 8: One building is chaos; the grid is calm
A single building’s demand jumps around wildly. Average enough of them and it settles into something smooth and predictable.

## Slide 9: Why so many energy optimisation projects fail
Too complex: models that capture every detail need data the utility doesn’t have and an expert to babysit. When the grid changes, they quietly go stale.
Too brittle: they shine in the demo, then break on the first messy week of real SCADA. Operators stop trusting them — and trust doesn’t come back.
And all of that costs money to build and keep alive. Energy is a big industry on thin margins, run by engineers who can think and count — charge X a year and save barely more than X, and they will know. The value has to clearly beat the cost.

## Slide 10: The RACE collaboration
RACE grew from deep domain knowledge in district heating — and from working alongside the people who run these grids. They are the real experts; no model is any good without them. The best results come with the operators in the loop, not replaced by it.
An EUDP-funded collaboration led by Glaze, with Aalborg University, Brønderslev Forsyning, Energy Cluster Denmark, DEVELCO and Agerkrantz Controls.

## Slide 11: A real grid: Brønderslev
Live on the Jyllandsgade section — 454 connected consumers — as part of the EUDP-funded RACE project with Aalborg University.
13 intelligent bypasses plus AI-based pressure control, taking setpoints from Beacon Tower through the plant’s existing SCADA.
A hydraulic optimisation: getting heat to where it’s needed more efficiently — without raising the temperature leaving the plant.
Brønderslev © tsca, CC BY-SA 3.0, via Wikimedia Commons

## Slide 12: The result
WINTER
7.3 %
less energy used
(degree-day corrected)
SUMMER
26.3 %
less energy used
(larger — still verifying why)
HEAT UTILISATION
+2.7 pts winter
+3.3 pts summer
more delivered heat
reaches consumers
Live on a real grid — measured and validated independently by Aalborg University, part of the
EUDP-funded RACE project. Achieved without raising the flow temperature leaving the plant.

## Slide 13: What we learned
The gains showed up across the whole area — not just next to the hardware we installed. Better hydraulics help the system as a whole.
The grid was conservatively run to begin with — which is exactly why there was so much to gain. Most small and mid-size grids are run the same way.
Summer losses are structurally high — low demand means water sits and goes stale, so standby losses dominate. That is why summer had more to recover here. But 26% is not a promise for every grid.

## Slide 14: The opportunity is the small grids
The big grids are already run tight — they have the money, the staff and the incentive to optimise. There’s no product for a market that already solves its own problem. The opening is the many small and mid-size grids, which are conservatively run and rarely optimised.
This is what Glaze was built for: cheap and automated from the start — function first, not bells and whistles.

## Slide 15
Kalmar’s Moskogen: ~360 GWh of heat a year — one “Moskogen”

## Slide 16: This is a fast-moving moment
RACE 2.0 is live now: two new Danish grids, with RACE also heading to Swedish grids — as we bring it to market as a product.
We’re adding demand-side management, targeting 10%+ yearly savings even as networks grow — using the heat already stored in buildings and pipes to spread demand in time, so the system serves everyone without over-building for the worst hour.
Same principle throughout: start simple, stay cheap, earn trust before adding complexity.

## Slide 17: The city breathes
Heat demand runs in cycles — and any single moment is almost impossible to predict. Together, across a grid, it averages out.
Most district heating can run far leaner than it does today.
A genuinely interesting problem — with real potential, if it is done simply and well.

## Slide 18: Thank you
See for yourself: the slides, the open datasets behind every chart, the code that makes them, and the reports we base our claims on — all here.
github.com/beacontower/techheads2026